## Worksheet
Field Type | Name Attribute | Unit | Description | Value | Required | Example | Version | Used For
configuration | id |  | Reference id for measurement data node |  | x | <device id=“1“ type=“battery“> | 2.0.1
configuration | type |  | device type | battery | x | <device id=“1“ type=“battery“> | 2.0.1
configuration | uid |  | device unique identifier |  | x | <uid>BAT12345</uid> | 2.0.1
configuration | name |  | device name |  |  | <name>Battery A</name> | 2.0.1
configuration | serial |  | device serial |  |  | <serial>BAT11.22.33</serial> | 2.0.1
configuration | vendor |  | device vendor |  |  | <vendor>vendor 123</vendor> | 2.0.1
configuration | model |  | device model |  |  | <model></model> | 2.0.1
configuration | address |  | bus address |  |  | <address>1</address> | 2.0.1
configuration | firmware |  | device firmware |  |  | <firmware>1.23.3</firmware> | 2.0.1
datapoints | B_CAPACITY | Ah | Nominal capacity (Only used for small support batteries. Use configuration value for BESS.)
datapoints | B_DOD | % | Depth of discharge |  | desired |  |  | Operational Reporting, Age Monitoring
datapoints | B_E_CHARGE_AC | kWh | Chargeable Energy AC |  | desired |  |  | Energy Monitoring
datapoints | B_E_CHARGE_DC | kWh | Chargeable energy DC |  | desired |  |  | Energy Monitoring
datapoints | B_E_DISCHARGE_AC | kWh | Dischargeable Energy AC |  | desired |  |  | Energy Monitoring
datapoints | B_E_DISCHARGE_DC | kWh | Dischargeable energy DC |  | desired |  |  | Energy Monitoring
datapoints | B_E_EXP | kWh | Energy export from storage system DC |  | desired |  |  | Energy Monitoring
datapoints | B_E_EXP_AC | kWh | Energy export from storage system AC |  | desired |  |  | Energy Monitoring
datapoints | B_E_IMP | kWh | Energy import to storage system DC |  | desired |  |  | Energy Monitoring
datapoints | B_E_IMP_AC | kWh | Energy import to storage system AC |  | desired |  |  | Energy Monitoring
datapoints | B_E_INT_EXP | kWh | Energy export from storage system (interval) DC
datapoints | B_E_INT_EXP_AC | kWh | Energy export from storage system (interval) AC
datapoints | B_E_INT_IMP | kWh | Energy import to storage system (interval) DC
datapoints | B_E_INT_IMP_AC | kWh | Energy import from storage system (interval) AC
datapoints | B_E_STORED | kWh | Currently stored energy |  | desired |  |  | Energy Monitoring
datapoints | B_FCE_COUNT |  | FCE count (full cycle equivalent)
datapoints | B_INV_COUNT |  | Number of connected inverters
datapoints | B_I_AC | A | Battery AC current |  | desired |  |  | Safety Monitoring
datapoints | B_I_CELL_MAX[1..x]_[1..x] | A | Maximum cell current |  | desired |  |  | Safety Monitoring
datapoints | B_I_CELL_MAX_CELL_INDEX |  | Index of the cell with the highest cell current
datapoints | B_I_CELL_MAX_MODULE_INDEX |  | Index of the module with the highest cell current
datapoints | B_I_CELL_MAX_RACK_INDEX |  | Index of the rack with the highest cell current
datapoints | B_I_CELL_MIN[1..x]_[1..x] | A | Minimum cell current |  | desired |  |  | Safety Monitoring
datapoints | B_I_CELL_MIN_CELL_INDEX |  | Index of the cell with the lowest cell current
datapoints | B_I_CELL_MIN_MODULE_INDEX |  | Index of the module with the lowest cell current
datapoints | B_I_CELL_MIN_RACK_INDEX |  | Index of the rack with the lowest cell current
datapoints | B_I_DC | A | Battery current DC |  | desired |  |  | Safety Monitoring
datapoints | B_I_DIS_DC | A | Discharging current DC
datapoints | B_LIM_I_CHARGE | A | Maximum charging current
datapoints | B_LIM_I_DISCHARGE | A | Maximum discharging current
datapoints | B_LIM_P_CHARGE | W | Maximum charging power
datapoints | B_LIM_P_DISCHARGE | W | Maximum discharging power
datapoints | B_LIM_U_CHARGE | V | Charge end voltage
datapoints | B_LIM_U_DISCHARGE | V | Discharge end voltage
datapoints | B_LOGIC_BAT_COUNT |  | Number of connected logical batteries (combination of racks)
datapoints | B_OT_TOTAL | h | Operating Hours
datapoints | B_P_DC | W | Total battery power |  | desired |  |  | Energy status monitoring
datapoints | B_RECTTIFIER_TOT_I_DC | A | Total current of rectifiers
datapoints | B_RECTTIFIER_TOT_P_DC | kW | Total battery rectifier dc power
datapoints | B_RECTTIFIER_TOT_U_DC_PCS | V | Total voltage of rectifiers PCS_DC side
datapoints | B_SOC | % | State of Charge |  | x |  |  | Safety Monitoring
datapoints | B_SOCH | % | State of charge (nominal capacity)
datapoints | B_SOC_CELL_MAX[1..x]_[1..x] | % | Maximum cell state of charge (SoC) |  |  |  |  | Safety Monitoring
datapoints | B_SOC_CELL_MAX_CELL_INDEX |  | Index of the cell with the highest cell SoC
datapoints | B_SOC_CELL_MAX_MODULE_INDEX |  | Index of the module with the highest cell SoC
datapoints | B_SOC_CELL_MAX_RACK_INDEX |  | Index of the rack with the highest cell SoC
datapoints | B_SOC_CELL_MIN[1..x]_[1..x] | % | Minimum cell state of charge (SoC) |  |  |  |  | Safety Monitoring
datapoints | B_SOC_CELL_MIN_CELL_INDEX |  | Index of the cell with the lowest cell SoC
datapoints | B_SOC_CELL_MIN_MODULE_INDEX |  | Index of the module with the lowest cell SoC
datapoints | B_SOC_CELL_MIN_RACK_INDEX |  | Index of the rack with the lowest cell SoC
datapoints | B_SOE | % | State of energy of a battery unit |  |  |  |  | monitoring, manage energy trading
datapoints | B_SOH | % | State of health |  | desired |  |  | Operational Reporting, Age Monitoring
datapoints | B_T_CELL[1..x]_[1..x]_[1..x] | °C | Cell temperature [°C]
datapoints | B_T_CELL_AVG[1..x]_[1..x] | °C | Average cell temperature |  | desired |  |  | Safety Monitoring
datapoints | B_T_CELL_MAX[1..x]_[1..x] | °C | Maximum cell temperature [°C] |  | desired |  |  | Safety Monitoring
datapoints | B_T_CELL_MAX_CELL_INDEX |  | Index of the cell with the highest cell temperature
datapoints | B_T_CELL_MAX_MODULE_INDEX |  | Index of the module with the highest cell temperature
datapoints | B_T_CELL_MAX_RACK_INDEX |  | Index of the rack with the highest cell temperature
datapoints | B_T_CELL_MIN[1..x]_[1..x] | °C | Minimum cell temperature [°C] |  | desired |  |  | Safety Monitoring
datapoints | B_T_CELL_MIN_CELL_INDEX |  | Index of the cell with the lowest cell temperature
datapoints | B_T_CELL_MIN_MODULE_INDEX |  | Index of the module with the lowest cell temperature
datapoints | B_T_CELL_MIN_RACK_INDEX |  | Index of the rack with the lowest cell temperature
datapoints | B_T_M[1..x]_[1..x] | °C | Module temperature [°C] |  | desired |  |  | Safety Monitoring
datapoints | B_T_M_MAX[1..x] | °C | Maximum module temperature [°C] |  | desired |  |  | Safety Monitoring
datapoints | B_T_M_MAX_INDEX_[1-9][0-9]{0,2} |  | Index of the module with the highest temperature in rack X
datapoints | B_T_M_MAX_RACK_INDEX |  | Index of the rack with the highest module temperature
datapoints | B_T_M_MIN[1..x] | °C | Minimum module temperature [°C] |  | desired |  |  | Safety Monitoring
datapoints | B_T_M_MIN_INDEX_[1-9][0-9]{0,2} |  | Index of the module with the lowest temperature in rack X
datapoints | B_T_M_MIN_RACK_INDEX |  | Index of the rack with the lowest module temperature
datapoints | B_T_U[1..x] | °C | Temperature Outside/ Ambient [°C] |  | desired
datapoints | B_U_AC | V | Battery AC voltage |  | desired |  |  | Safety Monitoring
datapoints | B_U_BULK | V | Battery charging voltage DC
datapoints | B_U_CELL[1..x]_[1..x]_[1..x] | V | Cell voltage
datapoints | B_U_CELL_AVG | V | Average cell voltage |  | desired |  |  | Safety Monitoring
datapoints | B_U_CELL_MAX[1..x]_[1..x] | V | Maximum cell voltage |  | desired |  |  | Safety Monitoring
datapoints | B_U_CELL_MAX_CELL_INDEX |  | Index of the cell with the highest cell voltage
datapoints | B_U_CELL_MAX_MODULE_INDEX |  | Index of the module with the highest cell voltage
datapoints | B_U_CELL_MAX_RACK_INDEX |  | Index of the rack with the highest cell voltage
datapoints | B_U_CELL_MIN[1..x]_[1..x] | V | Minimum cell voltage |  | desired |  |  | Safety Monitoring
datapoints | B_U_CELL_MIN_CELL_INDEX |  | Index of the cell with the lowest cell voltage
datapoints | B_U_CELL_MIN_MODULE_INDEX |  | Index of the module with the lowest cell voltage
datapoints | B_U_CELL_MIN_RACK_INDEX |  | Index of the rack with the lowest cell voltage
datapoints | B_U_DC | V | Battery voltage |  | desired |  |  | Safety Monitoring
datapoints | B_U_OC | V | Open circuit voltage
datapoints | B_WORKING_M_COUNT |  | Total number of working battery modules in a rack
datapoints | OP_STATE |  | Battery operational state, 1: Disconnected 2: Initializing 3: Connected 4: Standby 5: SOC Protection 6: Suspending 7: Discharging 8: Charging 99: Fault |  | desired |  |  | Availability monitoring
datapoints | T[1..x] | °C | Temperatures
datapoints | STATE[1..x] |  | Global battery state conditions |  | desired |  |  | device event monitoring and alarming
datapoints | ERROR[1..x] |  | Latest battery error code within the interval |  |  |  |  | Availability monitoring
datapoints | QS_TX |  | Telegrams transmitted (communication quality)
datapoints | QS_RX |  | Telegrams received (communication quality)
deprecated datapoints | B_F_AC | Hz | Grid frequency, use F_AC on inverter side instead
deprecated datapoints | B_P_AC | W | Battery power AC, use P_AC on inverter side instead
deprecated datapoints | B_Q_AC | var | Battery reactive power AC, use Q_AC on inverter side instead
deprecated datapoints | B_S_AC | VA | Battery apparent power AC, use S_AC on inverter side instead