## Worksheet
Field Type | Name Attribute | Unit | Description | Value | Required | Example | Version
configuration | id |  | Reference id for measurement data node |  | x | <device id=“1“ type=“power-plant-controller“> | 2.1.3
configuration | type |  | device type | power-plant-controller | x | <device id=“1“ type=“power-plant-controller“> | 2.1.3
configuration | uid |  | device unique identifier |  | x | <uid>PPC12345</uid> | 2.1.3
configuration | name |  | device name |  |  | <name>ppc device A</name> | 2.1.3
configuration | serial |  | device serial |  |  | <serial>PPC11.22.33</serial> | 2.1.3
configuration | vendor |  | device vendor |  |  | <vendor>vendor 123</vendor> | 2.1.3
configuration | model |  | device model |  |  | <model></model> | 2.1.3
configuration | address |  | bus address |  |  | <address>1</address> | 2.1.3
configuration | firmware |  | device firmware |  |  | <firmware>1.23.3</firmware> | 2.1.3
datapoints | PPC_BAT_PF_CTRL |  | Power factor correction value (battery)
datapoints | PPC_BAT_P_AC_INV | W | Sum of inverter active power (battery)
datapoints | PPC_BAT_P_CTRL_REL | % | Active power correction value (battery)
datapoints | PPC_BAT_Q_AC_INV | var | Sum of inverter reactive power (battery)
datapoints | PPC_BAT_Q_CTRL_REL | % | Reactive power correction value (battery)
datapoints | PPC_BAT_SOC | % | State of charge
datapoints | PPC_PF |  | Actual power factor
datapoints | PPC_PF_SET |  | Power factor setpoint
datapoints | PPC_PV_PF_CTRL |  | Power factor correction value (PV)
datapoints | PPC_PV_P_AC_INV | W | Summe Wechselrichter-Wirkleistung (PV)
datapoints | PPC_PV_P_CTRL_REL | % | Active power correction value (PV)
datapoints | PPC_PV_Q_AC_INV | var | Sum of inverter reactive power (PV)
datapoints | PPC_PV_Q_CTRL_REL | % | Reactive power correction value (PV)
datapoints | PPC_P_AC | W | Actual active power |  | x
datapoints | PPC_P_AC_AVAIL | W | Actual theoretical available active power
datapoints | PPC_P_AC_GRIDOP_MAX | W | Maximum active power during curtailment (grid operator)
datapoints | PPC_P_AC_INV | W | Inverter active power
datapoints | PPC_P_AC_RPC_MAX | W | Maximum active power during curtailment (3rd party)
datapoints | PPC_P_SET_ABS | W | Absolute active power setpoint
datapoints | PPC_P_SET_CTRL_REL | % | Active power correction value
datapoints | PPC_P_SET_GRIDOP_ABS | W | Absolute active power setpoint (grid operator)
datapoints | PPC_P_SET_GRIDOP_REL | % | Active power setpoint (grid operator)
datapoints | PPC_P_SET_MANUAL_ABS | W | Absolute active power setpoint (manually)
datapoints | PPC_P_SET_MANUAL_REL | % | Relative active power setpoint (manually)
datapoints | PPC_P_SET_REL | % | Active power setpoint |  | x
datapoints | PPC_P_SET_RPC_ABS | W | Absolute active power setpoint (3rd party)
datapoints | PPC_P_SET_RPC_REL | % | Active power setpoint (3rd party)
datapoints | PPC_P_SET_STATIC_ABS | W | Absolute active power setpoint (static)
datapoints | PPC_P_SET_STATIC_REL | % | Relative active power setpoint (static)
datapoints | PPC_Q_AC | var | Actual reactive power
datapoints | PPC_Q_AC_AVAIL | var | Actual theoretical available reactive power
datapoints | PPC_Q_SET_ABS | var | Absolute reactive power setpoint
datapoints | PPC_Q_SET_REL | % | Reactive power setpoint
datapoints | STATE[1..x] |  | Global power plant controller state conditions