## Worksheet
Field Type | Name Attribute | Unit | Description | Value | Required | Example | Version
configuration | id |  | Reference id for measurement data node |  | x | <device id=“1“ type=“inverter“> | 2.0.1
configuration | type |  | device type | inverter | x | <device id=“1“ type=“inverter“> | 2.0.1
configuration | uid |  | device unique identifier |  | x | <uid>INV12345</uid> | 2.0.1
configuration | name |  | device name |  |  | <name>Inverter A</name> | 2.0.1
configuration | serial |  | device serial |  |  | <serial>INV11.22.33</serial> | 2.0.1
configuration | vendor |  | device vendor |  |  | <vendor>vendor 123</vendor> | 2.0.1
configuration | model |  | device model |  |  | <model></model> | 2.0.1
configuration | address |  | bus address |  |  | <address>1</address> | 2.0.1
configuration | firmware |  | device firmware |  |  | <firmware>1.23.3</firmware> | 2.0.1
datapoints | A_IN[1..x] |  | Analogue input
datapoints | COS_PHI |  | Cos Phi actual value
datapoints | COS_PHI_LOAD[1..3] |  | Inductive or capacitive load (c/i)
datapoints | COS_PHI_NOM[1..3] |  | Cos Phi given value
datapoints | D_IN[1..x] |  | Digital input
datapoints | E_DAY | kWh | Energy generated per day
datapoints | E_INT | kWh | Energy generated per interval
datapoints | E_TOTAL | kWh | Total generated energy
datapoints | E_YEAR | kWh | Energy generated per year
datapoints | FT_AC_DAY | min | Feed in Time Day AC
datapoints | FT_AC_TOTAL | hour | Feed in Time Total AC
datapoints | F_AC[1..x] | Hz | Grid frequency (single phase or accumulated)
datapoints | I_AC[1..x] | A | Current AC (single phase or accumulated)
datapoints | I_DC[1..x] | A | Current DC (single input or accumulated)
datapoints | I_DC[1..x]_[1..x] | A | Current DC (single string)
datapoints | I_GDFI | mA | Earth leakage current
datapoints | OT_AC_DAY | min | Operation Time DAY
datapoints | OT_AC_TOTAL | hour | Operation Time TOTAL
datapoints | P_AC[1..3] | W | Power AC (single phase or accumulated) |  | x
datapoints | P_DC[1..x] | W | Power DC (single input or accumulated)
datapoints | Q_AC[1..3] | var | Reactive power (single phase or accumulated)
datapoints | R_AC | mOhm | Grid impedance
datapoints | R_ISO | kOhm | Isolation resistant
datapoints | S_AC[1..3] | VA | Apparent power (single phase or accumulated)
datapoints | T[1..x] | °C | inverter temperatures
datapoints | T_WR[1..x] | °C | inverter temperatures
datapoints | U_AC[1..3] | V | Voltage AC (single phase or accumulated)
datapoints | U_AC_L1L2 | V | Volts L1-L2
datapoints | U_AC_L2L3 | V | Volts L2-L3
datapoints | U_AC_L3L1 | V | Volts L3-L1
datapoints | U_DC[1..x] | V | Voltage DC (single input or accumulated)
datapoints | U_DC[1..x]_[1..x] | V | Voltage DC (single string)
datapoints | U_DC_NE | V | Voltage DC negative pole to earth
datapoints | U_DC_PE | V | Voltage DC positive pole to earth
datapoints | STATE[1..x] |  | Global inverter state conditions
datapoints | ERROR[1..x] |  | Global inverter error conditions
datapoints | QS_TX |  | Telegrams transmitted (communication quality)
datapoints | QS_RX |  | Telegrams received (communication quality)
deprecated datapoints | PC | % | Power Control